## Sheet1
category | description | unit | qty | rate | amount
PRELIMINARY | Initial Mobilization and final Demobilization of equipment and personnel to and from site from contractor’s base office. | LS | 1 | 150000 | 150000
PRELIMINARY | Inter sites Mobilization and Demobilization of equipment and personnel. | LS | 1 | 50000 | 50000
PRELIMINARY | Clearing of site | M2 | 100 | 400 | 40000
BOREHOLE DRILLING | Conduct geophysical survey (field work, interpretation and report to locate productive borehole sites, delineate aquiferous zones and identify horizons vulnerable to saltwater intrusion and mineralization) for the location of borehole at a suitable site. | LS | 1 | 70000 | 70000
BOREHOLE DRILLING | Drilling of borehole in basement/sedimentary formation | M | 120 | 6000 | 720000
BOREHOLE DRILLING | Supply and install 125mm diameter uPVC casings of 12 bar pressure rating. | M | 108 | 4500 | 486000
BOREHOLE DRILLING | Supply and install 125mm diameter uPVC screen of 12 bar pressure rating. | M | 12 | 4700 | 56400
BOREHOLE DRILLING | Supply and place approved gravel 5-10mm size for casings and screens below ground surface. | LS | 1 | 50000 | 50000
BOREHOLE DRILLING | Borehole cleaning and development till water is clear and silt free. | LS | 1 | 60000 | 60000
BOREHOLE DRILLING | Conduct continuous borehole pump test for not less than 6 hour period. | LS | 1 | 120000 | 120000
BOREHOLE DRILLING | Conduct water quality analysis (biological, chemical and physical) and borehole disinfection | LS | 1 | 70000 | 70000
BOREHOLE DRILLING | Provide and place cement grout down to 5m from surface to protect borehole from surface water. | LS | 1 | 80000 | 80000
BOREHOLE DRILLING | Supply and installation 212mm diameter x 3m height API steel pipe fitted in the grout for borehole to the depth of 3m below and welded with thick cover to serve as well head. Refer to DRAWING NO 2 | LS | 1 | 70000 | 70000
SOLAR PUMP AND POWER REQUIREMENTS | Supply and Install pump type SQ flex 3-105 + CU200 switch box. (Refer to pump and wattage table) branded or with engraving as specified by RUWASSA. NOTE: All pump cartons must be returned to the state RUWASSA office for destruction | Set | 1 | 950000 | 950000
SOLAR PUMP AND POWER REQUIREMENTS | Supply and Install 3M scotch cast Cable jointing kit & earthing | Set | 1 | 30000 | 30000
SOLAR PUMP AND POWER REQUIREMENTS | Supply & Install Solar mono/polycrystalline panels as in TSS | Watts | 2000 | 220 | 440000
SOLAR PUMP AND POWER REQUIREMENTS | Supply & Install Support Structure and frame for panels as in drawing no 3&6 | NR | 1 | 170000 | 170000
SOLAR PUMP AND POWER REQUIREMENTS | Supply and Install 4X6mm2 pump motor cables | M | 120 | 1500 | 180000
SOLAR PUMP AND POWER REQUIREMENTS | Supply and Install 4mm2 inter-connector cables( Nigeria Cables) | Set | 1 | 50000 | 50000
SOLAR PUMP AND POWER REQUIREMENTS | Supply and Install Marine rope (10mm) as antidrop for the pump | M | 120 | 200 | 24000
SOLAR PUMP AND POWER REQUIREMENTS | Supply and Install High pressure 32mm uPVC piping (8bar) for pump installation | M | 110 | 1700 | 187000
SOLAR PUMP AND POWER REQUIREMENTS | Supply and Install Locally assembled lightening protection set (with a hard drawn high conductivity copper tape of 1 x 3mm), using made in UK accessories. | Set | 1 | 20000 | 20000
SOLAR PUMP AND POWER REQUIREMENTS | Supply and Install level switch | Set | 1 |  | 0
SOLAR PUMP AND POWER REQUIREMENTS | Construct & Install security for the solar pump including reinforced concrete box on the 2 stage opening metal box over the the well head. Note that this MUST be completely underground (REFER TO THE DRAWING No 1&2) | LS | 1 | 120000 | 120000
TANK AND STANCHION | Excavate:1200mmx1200mmx900mm for pad footings | NR | 4 | 10000 | 40000
TANK AND STANCHION | 100mm thick blinding on pad foundations | m3 | 0.6 | 30000 | 18000
TANK AND STANCHION | Pad footing (1200mmx1200mm x900mm) | m3 | 5.2 | 21000 | 109200
TANK AND STANCHION | Reinforcements for the pad(5 lengths of starter bars Y22 dia with threaded ends and 5.5 lengths of Y16 for mersh) as in drawings no 7 | length | 11.5 | 12000 | 138000
TANK AND STANCHION | Provide base plate 500mmx500mm with 4no, 22.5mm dia.holes (16mm thick) | NR | 4 | 49000 | 196000
TANK AND STANCHION | Provide 152mmx152mmx37kg/m UC (H-Channel); welded, braced and bolted to 16mm base plate | M | 28 | 27000 | 756000
TANK AND STANCHION | Provide 152mmx152mmx37kg/m as primary beams | M | 7.8 | 27000 | 210600
TANK AND STANCHION | Provide 152mmx152mmx37kg/m as secondary beams | M | 18 | 27000 | 486000
TANK AND STANCHION | 60X60X6mm angle bars for brazing & rail | M | 102 | 2400 | 244800
TANK AND STANCHION | 60X60X6mm angle bars for brazing | M | 45 | 2400 | 108000
TANK AND STANCHION | 25mm steel grating 100mmx50mm | m2 | 11.7 | 48000 | 561600
TANK AND STANCHION | Allow for steel ladder cage, hand rails | LS | 1 | 150000 | 150000
TANK AND STANCHION | Bolts, gusset plate, angle iron and connection/ plate accessories | LS | 1 | 90000 | 90000
TANK AND STANCHION | Prepare tower to receive paint (scrapping, brushing & cleaning rust and dirt), treat with 3 coats of red oxide and apply 3 coats of approved paint (Berger or equivalent) on tower (Aluminium colour) | LS | 1 | 120000 | 120000
TANK AND STANCHION | Supply and install approved 4,000Litres BLACK PVC tank and complete with technical specifications requirements | NR | 2 | 200000 | 400000
PLUMBING, TAP ISLAND AND RETICULATION | Excavate trench 600mmx600mm to receive pvc water distribution pipes to tank location. | M | 30 | 800 | 24000
PLUMBING, TAP ISLAND AND RETICULATION | Pipe 32mm water inlet pvc pipes from the borehole location to tank, complete with accessories | M | 30 | 2100 | 63000
PLUMBING, TAP ISLAND AND RETICULATION | Excavate trench (600mm×600mm) and lay Pipe 4 bar 50mm pressure pipe from tank to 6 locations (Tap Islands) in the host community (Priotising the school) , total cummulative distance of 0.8km | M | 800 | 890 | 712000
PLUMBING, TAP ISLAND AND RETICULATION | Provide and install 25mm diameter double head 3 stand posts with (6) PVC sprouts embedded in concrete tap island as contained in drawing no 4 complete with inspection chambers (for the reticulation), control valve chambers, drainages and soak pit at every 150m in the reticulation line | NR | 6 | 180000 | 1080000
PLUMBING, TAP ISLAND AND RETICULATION | Flush and disinfect the whole system (tank, pipes and reticulation line) using high test hypochlorite (HTH) and test run the whole system | LS | 1 | 80000 | 80000
PLUMBING, TAP ISLAND AND RETICULATION | Provide 5 copies of spiral bound report of work with a soft copy on CD | COPY | 5 | 1000 | 5000
EXCAVATION AND EARTH WORK | Excavate trench to receive fence foundation 600mmx450mmx 50meters total perimeter | m3 | 8.1 | 1000 | 8100
EXCAVATION AND EARTH WORK | Backfill and ram foundation spread and remove surplus excavated materials from site | m3 | 5 | 600 | 3000
CONCRETE WORK | Pour concrete 1:2:4 in footing for GI pipes 450mmx450mmx 600mm (13 Nr) | m3 | 2 | 20000 | 40000
CONCRETE WORK | Pour concrete 1:2:4 in wall footing 150mm thick | m3 | 1.7 | 23000 | 39100
CONCRETE WORK | Provide Coping 50mm thick 250mm wide on top of block work | m3 | 0.5 | 20000 | 10000
CONCRETE WORK | Pour concrete 1:3:6 in Floor 75mm thick of the entire fenced area (covering both the wellhead security) | m3 | 4.3 | 120000 | 516000
BLOCK WORK | Install 150mm sandcrete blocks 450mm high the specified perimeter at sub-structure | m2 | 11 | 32000 | 352000
BLOCK WORK | Install 150mm sandcrete blocks 450mm high the specified perimeter at super-structure | m2 | 14 | 3400 | 47600
FORM WORK | Sides and soffits of copping | m | 7.5 | 1200 | 9000
METAL WORK | Provide see through metal gate, using GI wire mesh. | nr | 1 | 150000 | 150000
METAL WORK | Provide and install 2inches pipes (GI) (3m length) | nr | 13 | 23000 | 299000
METAL WORK | Provide and install wire guaze (GI) 2m high round the entire area. | m2 | 60 | 2300 | 138000
METAL WORK | Provide Binding wire | kg | 5 | 40000 | 200000
METAL WORK | Provide Steel spikes on coping | ls | 1 | 1200 | 1200
FINISHES | Rendering entire block work, in and out | m2 | 28 | 1300 | 36400
SIGNBOARD | Provide metal sheet, 1200mm x1050mm sheet (2mm gauge) | NR | 1 | 1000 | 1000
SIGNBOARD | Provide 3200mmx62.5mm diameter GI Pipe, BS, 3mm gauge for signboard stands | NR | 2 | 25000 | 50000
SIGNBOARD | Provide 25mmx25mm square metal pipe (2mm gauge), for support and framing around signboard edges. | NR | 1 | 30000 | 30000
SIGNBOARD | Paint, white, gloss, dulux brand, for background (1.3 ltrs); Paint, black, gloss, dulux brand, for stands (1.3 ltrs) and Paint, blue, gloss, dulux brand, for border lines (1.3 ltrs) | Ltrs | 3.9 | 5000 | 19500
SIGNBOARD | Materials and Labour for art works and paintings including 3-coats of antirust [Art works to include same write-up on both sides of the signboard and to be neatly done with paints of specified quality and colour] | LS | 1 | 40000 | 40000
SIGNBOARD | Labour for cutting, bracing and welding | LS | 1 | 60000 | 60000
SIGNBOARD | Allow for delivery to site and installation, including accessories (nuts, bolts, etc.) | LS | 1 | 40000 | 40000